KURUMAN TAXI RANK

ELECTRICAL INSTALLATIONS

SECTION 3:  SCHEDULES

INDEX

Item		Description	Page

1.	General 	       22

2.	Schedule of Cables 	       22

3.	Schedule of Light Fittings 	       23

4.	Power Skirting………………………………………………………………….		  24

5.	Schedule of Socket Outlets	      24

KURUMAN TAXI RANK

ELECTRICAL INSTALLATION

SECTION 3:  SCHEDULES

  - GENERAL

This section of the specification forms part of and must be read in conjunction with the general and supplementary specification, as well as the drawings.

  - SCHEDULE OF CABLES.

|  |  | DB Section |  |
| --- | --- | --- | --- |
| From | To | Normal | Back-up |
| Substation | DB-BUS | 25sqmm 4C | n/a |
| DB-BUS | SL1 | 6sqmm 3C | n/a |
| DB-BUS | SL7 | 6sqmm 3C | n/a |
| Substation | DB-1 | 95sqmm 4C | n/a |
| DB-1 | DB-2 | 16sqmm 4C | 16sqmm 4C |
| DB-1 | DB-4 | 25sqmm 4C | 10sqmm 4C |
| DB-2 | DB-3 | 6sqmm 4C | 6sqmm 4C |
| DB-2 | DB-5 | 10sqmm 4C | 10sqmm 4C |
| DB-5 | DB-6 | 10sqmm 4C | 6sqmm 4C |
| DB-5 | SL3-SL6 | 6sqmm 4C | n/a |
| DB-6 | DB-7 | 10sqmm 4C | n/a |
| DB-6 | SL2 | 6sqmm 3C | n/a |
| DB-7 | SL8-SL12 | 6sqmm 4C | n/a |
| Generator | DB-4 | 25sqmm 4C | n/a |

  - SCHEDULE OF LIGHT FITTINGS

The light fittings and accessories are to be according to the quality specifications in Part 3 and shall be approved by the Engineer and shall be of types:

| Specification | Brand |
| --- | --- |
| 250W LED light on 12m street light pole. IP65 250W LED streetlight with an efficacy of at least 150 lumens per Watt, an L-70 output life-hours of at least 50 000, and a 5year warranty. The fitting shall be complete with a flicker-free driver. CRI: >70​ | Genesis One Rigel 36 |
| 100W LED light mounted on wall. IP65 100W LED streetlight light with an efficacy of at least 150 lumens per Watt, an L-70 output life-hours of at least 50 000, and a 5year warranty. The fitting shall be complete with a flicker-free driver. CRI: >70 | Genesis One Rigel 36 |
| White 36W 600mm x 600mm ceiling-recessed LED panel light with a 120º beam angle, an efficacy of at least 120 lumens per Watt, a glare rating (UGR) of less than 19, an L-70 output life-hours of at least 50 000, and a 5year warranty. The fitting shall be complete with a flicker-free driver and a 3m cord and a with 6A SANS 164-3 plug. | Genesis One Corvis |
| Black IP65, IK10, 18W LED surface-mount bulkhead light with a 110º beam angle, an output of at least 1780 lumens, a light temperature of 4000K, an L-70 life-hours of 50 000. The fitting shall be of a die-cast Aluminium housing and a UV stabilised diffuser and shall have a tamper-proof connector. | Gensis One Subra 65 |
| White 13W LED downlight recessed in ceiling or slab, with a 36º beam angle, an efficacy of at least 110 lumens per Watt, a glare rating (UGR) of less than 19, a light temperature of 4000K, an L-70 output life-hours of at least 50 000, and a 3-year warranty. The fitting shall be complete with a flicker-free driver and a polycarbonate opal diffuser and mounting accessories. | Gensis One Estrela 178 |
| White 40W 1.2m linear LED light with a IP65 polycarbonate, IK10 impact-resistant housing and a polycarbonate optical lens. The fitting shall have an efficacy of at least 130 lumens per Watt, an L-70 life-hours of at least 50 000 and a 5-year warranty. The light fitting shall be a Genesis One Genproof 68 LED batten or an approved equivalent. | Gensis One Genproof 68 |
| 100W LED surface mount bay light. IP65 100W LED bay light with an efficacy of at least 150 lumens per Watt, an L-70 output life-hours of at least 50 000, and a 5year warranty. The fitting shall be complete with a flicker-free driver. CRI: >70 | Gensis One Genbay |

  - POWER SKIRTING

Power Skirting shall be of tow tier powder-coated steel, Cabstrut or equivalent (equivalent to be approved by Engineer prior).

  - SCHEDULE OF SOCKET OUTLETS AND LIGHT SWITCHES

| Type | Specification |
| --- | --- |
| Normal wall flush-mount | SANS 164-1 & SANS 164-2 combo, steel white enamel coated - Crabtree Classic |
| 2A Current limited | SANS 164-1 & SANS 164-2 combo, with 2A MCB steel white enamel coated - Crabtree Classic. |
| Normal surface-mount | SANS 164-1, steel white enamel coated - Crabtree Classic |
| Dedicated wall flush-mount | SANS 164-4, steel red enamel coated - Crabtree Classic |
| Normal power skirting mount - 1 | SANS 164-1, steel powder-coated - Cabstrut |
| Normal power skirting mount - 2 | SANS 164-2, steel powder-coated - Cabstrut |
| Dedicated power skirting mount | SANS 164-4, steel powder-coated - Cabstrut |

Circuits for socket outlets shall be supplied with 4mm2 PVC insulated stranded copper wire and 2,5mm2 PVC insulated copper earth wire.

THIS PAGE WAS INTENTIONALLY LEFT BLANK