KURUMAN TAXI RANK

ELECTRICAL INSTALLATIONS

SECTION 1: GENERAL SPECIFICATION

I N D E X

Item		Description	Page

1.1	Regulations, Factories Act and By-Laws	  2

1.2	Notices and Fees	  2

1.3	Schedule of Fittings	  2

1.4	Quality of Materials	  2

1.5	Conduit and Accessories 	  3

1.6	Conduit in roof Spaces	  4

1.7	Surface Mounted Conduit 	  4

1.8	Conduit in Concrete Slabs	  5

1.9	Flexible Connections for Connections to Gysers, Machines etc.	  6

1.10	Wiring 	  6

1.11	Switches and socket outlets	  6

1.12	Switchgear	  7

1.13	Switchboard	  7

1.14	Workmanship and Staff 	  7

1.15	Earthing of Installation 	  8

1.16 	Mounting and Positioning of Light Fittings 	  8

1.17	Variations in Extent of Contract 	  8

1.18	Employer’s Material 	  9

KURUMAN TAXI RANK

ELECTRICAL INSTALLATION

SECTION 1: GENERAL SPECIFICATION

1.1		REGULATIONS, FACTORIES ACT AND BY-LAWS

The work shall be carried out strictly in accordance with:

(a)	the latest issue of "SANS 0142 : Code of Practice for the Wiring of Premises" hereafter called the "Wiring Code".

(b)	the "Occupational Health and Safety Act" of 1993 as amended to date and hereafter called the "Act".

(c)	the Municipal By-Laws and any special requirements of the local Supply Authority.

(d)	the local Fire Office Regulations.

In addition, the work is to be of high standard and to the satisfaction of the Engineer.

1.2		NOTICES AND FEES

The Contractor shall give all notices required by and pay all necessary fees, including any inspection fees, which may be due to the local Supply Authority.

At submittal of the official account, only the nett amount of the fee charged by the Supply Authority for connection of the installation to the supply mains, will be refunded to the Contractor by the Client.

1.3		SCHEDULE OF FITTINGS

In all instances where schedules of light, socket outlet and power points are attached or included on the drawings, these schedules are to be regarded as forming part of the specifications.

1.4		QUALITY OF MATERIALS

Only materials of first class quality shall be used and all materials shall be subject to the approval of the Engineer.

Wherever applicable the material is to comply with the relevant South African Bureau of Standards specifications, or to British Standard Specifications, where no SANS specifications exist.

Materials wherever possible, must be of South African Manufacture.

1.5		CONDUIT AND ACCESSORIES

The type of conduit and accessories required for the service, i.e. whether the conduit and accessories shall be of the screwed type, plain-end type or of the non-metallic type and whether metallic conduit shall be black enamelled or galvanised, is specified in Part 2  of this specification.

Unless other methods of installation are specified for certain circuits, the installation shall be in conduit throughout.  No open wiring in roof spaces or elsewhere will be permitted.

The conduit and conduit accessories shall comply fully with the applicable SANS specifications as set out below and the conduit shall bear the mark of approval of the South African Bureau of Standards.

a)	Screwed metallic conduit and accessories:  SANS 1065, parts 1 and   2.

b)	Plain-end metallic conduit and accessories:  SANS 1065, parts 1 and 2.

c)	Non-metallic conduit and accessories:  SANS 950

All conduit fittings except couplings, shall be of the inspection type.  Where cast metal conduit accessories are used, these shall be of malleable iron.  Zinc base fittings will not be allowed.

Bushes used for metallic conduit shall be brass and shall be provided in addition to locknuts at all points where the conduit terminates at switchboards, switch-boxes, draw-boxes, etc.

Draw-boxes are to be provided in accordance with the “Wiring Code” and wherever necessary to facilitate easy wiring.

For light and socket outlet circuits, the conduit used shall have an external diameter of 20mm.  In all other instances the sizes of conduit shall be in accordance with the “Wiring Code”  for the specified number and size of conductors, unless otherwise directed in part 2 of this specification or indicated on the drawings.

Only one manufactured type of conduit and conduit accessories will be permitted throughout the installation.

Running joints in screwed conduit are to be avoided as far as possible and all conduit systems shall be set or bent to the required angles.  The use of normal bends must be kept to a minimum with exception of larger diameter conduits where the use of such bends is essential.

All metallic conduit shall be manufactured of mild steel with a minimum thickness of 1,2mm for plain-end conduit and 1,6mm in respect of screwed conduit.

Under no circumstances will conduit having a wall thickness of less than 1,6mm be allowed in screeding laid on top of concrete slabs.

Bending and setting of conduit must be done with special bending apparatus manufactured for the purpose and which are obtainable from the manufacturers of the conduit systems.  Damage to conduit resulting from the use of incorrect bending apparatus or methods applied must on indication by the Client’s inspectorate staff, be completely removed and rectified and any wiring already drawn into such damaged conduits must be completely renewed at the Contractor’s expense.

Conduit and conduit accessories used for flame-proof or explosion-proof installations and for the suspension of luminaires as well as all load bearing conduit shall in all instances be of the metallic screwed type.

All conduit and accessories used in areas within 50 km of the coast shall be galvanised to SANS 763.

Tenderers must ensure that general approval of the proposed conduit system to be used is obtained from the local electricity supply authority prior to the submission of their tender.  Under no circumstances will consideration be given by the Client to any claim submitted by the Contractor, which may result from a lack of knowledge in regard to the supply authority’s requirements.

1.6 		CONDUIT IN ROOF SPACES

Conduit in roof spaces shall be installed parallel or at right angles to the roof members and shall be secured at intervals not exceeding 1,5m by means of saddles screwed to the roof timbers.

Nail or crampets will not be allowed.

Where non-metallic conduit has been specified for a particular service, the conduit shall be supported and fixed with saddles with a maximum spacing of 450 mm.  The Contractor shall supply and install all additional supporting timbers in the roof space as required.

Under flat roofs, in false ceilings or where there is less than 0,9m of clearance, or should the ceilings be insulated with glass wool or other insulating material, the conduit shall be installed in such a manner as to allow for all wiring to be executed from below the ceilings.

Conduit runs from distribution boards shall, where possible terminate in fabricated sheet steel draw-boxes installed directly above or in close proximity to the boards.

1.7  		SURFACE MOUNTED CONDUIT

Wherever possible, the conduit installation is to be concealed in the building work; however, where unavoidable or otherwise specified under Part 2 of the specification, conduit installed on the surface must be plumbed or levelled and only straight lengths shall be used.

The use of inspection bends is to be avoided and instead the conduit shall be set uniformly and inspection coupling used where necessary.

No threads will be permitted to show when the conduit installation is complete, except where running couplings have been employed.

Running couplings are only to be used where unavoidable, and shall be fitted with a sliced couplings as a lock nut.

Conduit is to be run on approved spaced saddles rigidly secured to the walls.

Alternatively, fittings, tees, boxes, couplings etc., are to be cut into the surface to allow the conduit to fit flush against the surface.  Conduit is to be bedded into any wall irregularities to avoid gaps between the surface and the conduit.

Crossing of conduits is to be avoided, however, should it be necessary purpose-made metal boxes are to be provided at the junction.  The finish of the boxes and positioning shall be in keeping with  the general layout.

Where several conduits are installed side by side, they shall be evenly spaced and grouped under one purpose-made saddle.

Distribution boards, draw-boxes, industrial switches and socket outlets etc., shall be neatly recessed into the surface to avoid double sets.

In situations where there are no ceilings the conduits are to be run along the wall plates and the beams.

Painting of surface conduit shall match the colour of the adjacent wall finishes.

Only approved plugging materials such as aluminium inserts, fibre plugs, plastic plugs, etc., and round-head screws shall be used for fixing saddles, switches, socket outlets, etc., to walls, wood plugs and the plugging in joints in brick walls are not acceptable.

1.8		CONDUIT IN CONCRETE SLABS

In order not to delay building operations the Contractor must ensure that all conduits and other electrical equipment which are to be cast in the concrete columns and slabs are installed in good time.

The Contractor shall have a representative in attendance at all times when the casting of concrete takes place.

Draw-boxes, expansion joint boxes and round conduit boxes are to be provided where necessary.  Sharp bends of any nature will not be allowed in concrete slabs.

Draw and/or inspection boxes shall be grouped under one common cover plate, and must preferable be installed in passages or male toilets.

All boxes, etc., are to be securely fixed to the shuttering to prevent displacement when concrete is cast.  The conduit shall be supported and secured at regular intervals and installed as close as possible to the neutral axis of concrete slabs and/or beams.

Before any concrete slabs are cast, all conduit droppers to switchboards shall be neatly spaced and rigidly fixed.

1.9		FLEXIBLE CONNECTIONS FOR CONNECTIONS TO STOVES, MACHINES  ETC.

Flexible tubing connections shall be of galvanised steel construction, and in damp situations of the plastic sheathed galvanised steel type.  Other types may only be used subject to the prior approval of the Client’s site electrical representative.

Connectors for coupling onto the flexible tubing shall be of the gland or screw-in types, manufactured of either brass or cadmium or zinc plated mild steel, and the connectors after having been fixed onto the tubing, shall be durable and mechanically sound.

Aluminium and zinc alloy connectors will not be acceptable.

1.10 		WIRING

Except where otherwise specified in Section 2 of the Specification, wiring shall be carried out in conduit throughout. Only one circuit per conduit shall be permitted.

No wiring shall be drawn into conduit until the conduit installation has been completed and all conduit ends provided with bushes. All conduit to be clear of moisture and debris before wiring is commenced.

Unless otherwise directed in Section 2 of the Specification or indicated on the drawings, all wiring for lighting circuits is to be carried out with 2,5mm² conductors and for the socket outlet circuits the wiring shall consist of 4mm² conductors with a 2,5mm² earth conductors. In all other instances the number and size of cables drawn into any conduit shall be as specified or shown on the drawings. Sizes and numbers of cables not specified must be determined in accordance with the "Wiring Code".

The loop-in system shall be followed throughout, and no  joints of any description will be permitted.

The wiring shall be done in PVC insulated 600/1000 V grade cable to SANS 150 (tables C & H).

Where cable ends connect onto switches, fittings, etc., the end strands must be neatly and tightly twisted together and firmly secured. Cutting away of wire strands of any cable will not be allowed.

1.11		SWITCHES AND SOCKET OUTLETS

All switches and switch-socket outlet combination units shall conform to the Employer’s Quality Specifications.

None other than 16 A 3-pin sockets are to be used, unless other special purpose types are distinctly specified or shown on the drawings.

All light switches shall be installed at 1400mm above finished floor level and all socket outlets as directed in the Schedule of socket outlet points and special power points, which forms part of this Specification, or alternatively the height of socket outlets may be indicated on the drawings.

1.12		SWITCHGEAR

Switchgear, which includes circuit breakers, iron-clad switches, interlocked switch-socket outlet units, contactors, time switches, etc., is to be in accordance with the Employer’s Quality Specifications and shall be equal and similar in quality to such brands as may be specified.

For uniform appearance of switchboards, only one approved make of each of the different classes of switchgear shall be used throughout the installations.

1.13		SWITCHBOARDS

All boards shall be in accordance with the types as specified, be constructed according to the detail or type drawings and must be approved before installation.

In all instances where provision is to be made on boards for supply authority’s main switch and/or metering equipment the Contractor must ensure that all requirements of the authorities concerned in this respect are met.

Any construction, or standard type board proposed as an alternative to that specified, must have the prior approval of the department.

All busbars, wiring, terminals, etc, are to be adequately insulated and all wiring is to enter the switchgear from the back of the board. The switchgear shall be mounted within the boards to give flush to the panel. Cable end boxes and other ancillary equipment must be provided where required.

Clearly engraved labels are to be mounted on or below every switch. The wording of the labels in English is to be according the lay-out drawings or as directed by the Employer’s Representative and must be confirmed on site. Flush mounted boards to be installed with the top of board 1800mm above the finished floor level.

1.14		WORKMANSHIP AND STAFF

All artisans employed on the service must be in possession of a Wireman's Certificate of Registration. Apprentices and Improvers, not in possession of this Certificate cannot be employed on the service without the prior approval of the Employer.

The workmanship shall be of the highest grade and to the satisfaction of the Employer and the Engineer

All inferior work shall, on indication by the Employer’s Inspecting Officers, immediately be removed and rectified by and at the expense of the Electrical Contractor.

1.15		EARTHING OF INSTALLATION

The type of main earthing must be as required by the supply authority, if other than the Employer, and in any event as directed by the Employer's Representative, who may require additional earthing to meet test standards.

Installations shall be effectively earthed in accordance with the "Wiring Code" and to the requirements of the supply authority.

All hot and cold water and waste pipes are to be effectively bonded by means of 12,5mm x 1,60mm solid or perforated copper tape (not wire), clamped by means of brass bolts and nuts. The tape is to be fixed to walls by means of rounded brass screws at intervals not exceeding 150mm.

1.16		MOUNTING AND POSITIONING OF LIGHT FITTINGS

The Electrical Contractor is to note that in the case of board and acoustic tile ceilings, i.e. as opposed to concrete slabs, close co-operation with the Building Contractor is necessary to ensure that as far as possible the light fittings are symmetrically positioned with regard to the ceiling pattern.

The layout of the fittings as indicated on the drawings must be adhered to as far as possible, but the exact positions must be confirmed with the Employer’s Representative.

Fluorescent fittings installed against concrete ceilings shall be screwed to the outlet boxes and in addition 2 x 6 mm expansion or other approved type fixing bolts are to be provided. The bolts are to be 3/4 of the length of the fittings apart.

Fluorescent fittings to be mounted on board ceilings shall be secured by means of two 40 mm x No. 10 round head screws and washers. The fittings shall also be bonded to the circuit conduit by means of locknuts and brass bushes. The fixing screws are to be placed 3/4 of the length of the fitting apart.

In addition to the above, an earth conductor is to be taken from the earthing terminal on all fluorescent fittings and solidly bonded onto the conduit installation.

Incandescent fittings are to be screwed directly to outlet boxes in concrete slabs. Against board ceilings the fittings shall be secured to the brandering or joints by means of two 40 mm x No. 8 round head screws.

Before any light luminaires are ordered by the Contractor, the makes and types of these luminaires must be approved by the Engineer.

1.17		VARIATIONS IN EXTENT OF CONTRACT

The Employer reserves the right to instruct the Contractor to carry out variations to the contract or in accordance with the prices quoted by the Contractor in the Price Schedule for Variations or Bill of Quantities, which ever is applicable.

For variations not provided for in the Price Schedule, or Bill of Quantities, the Employer may call on the Contractor to submit a separate written quotation.

Labour and material shall be based on items in the price schedule of the Contract, and no payment will be made for the transport of labour and material to and from the service.

The Employer, however, reserves the right to execute any alterations or additions that may be necessary with its own staff.

1.18		EMPLOYER’S MATERIAL

The Employer reserves the right to omit the supply of light luminaires, cooking appliances and water heaters from the contract in whole or in part, and to deliver such material to the Contractor from its own stores.

When certain materials are supplied by the Employer to the Contractor for installation, the Contractor must arrange for taking delivery and providing safe storage for these materials.

The Contractor will be held responsible for all damage to or loss of such material while it is in his custody.